NXZ(H)MN、NZ5(H)M、NXZ(H)BN、NZ5(H)B

Communication Protocol for Series Automatic Transfer Switching Devices

User Manual

Zhejiang CHINT Electrics Co., Ltd.

February 2025

Contents

Preface	1

- Scope	2

- Protocol Overview	2

  - Definitions and Terms	2

  - Physical layer	2

  - Data link layer	3

  - Application layer	3

- Function code	4

  - Read data register（03H）	4

  - Write data register（06H）	5

  - Error Handling	5

- Communication data registers	6

  - Dataset	6

  - Power frequency registers	8

  - Power status registers	8

  - Switch status registers	8

  - Control command registers	9

  - Forced transfer registers	9

- Communication connection method	10

  - Hardware connection	10

  - Communication parameter configuration	10

  - Communication anomaly troubelshooting	10

Appendix A CRC-16 generation principle	11

Appendix B NXZ(H)MN communication application cases	12

## Preface

This user manual is proposed by Zhejiang CHINT Electrics Co., Ltd.

The current version is V1.1. This user manual only represents the content of this version. Updates may not be notified. Please pay attention to the latest version from our company.

1 / 12

## NXZ(H)MN, NZ5(H)M, NXZ(H)BN, NZ5(H)B Series Automatic Transfer Switching Device Communication Protocol User Manual (Modbus-RTU)

#### Scope

This user manual specifies the physical connection, communication link, and application technical specifications between the automatic transfer switching device and the master station.

This user manual applies to T-type (communication-capable) automatic transfer switching products of the following eight series: NXZMN, NXZHMN, NZ5M, NZ5HM, NXZBN, NXZHBN, NZ5B, and NZ5HB.

#### Protocol Overview

The Modbus protocol is an industrial bus protocol designed based on the ISO/OSI model (7 layers), but it only uses three of the seven layers—the physical layer, data link layer, and application layer—thereby simplifying the protocol model and reducing the difficulty of use.

#### Definitions and Terminology

The following terms apply to this user manual.

- Open Systems Interconnection (OSI) Model

A standard established by the International Organization for Standardization (ISO) in 1984, aiming to provide a common foundation and standard framework for the interconnection of computers from different manufacturers.

- Physical Layer

The first layer in the Open Systems Interconnection (OSI) model, providing a physical link for achieving transparent transmission in communication.

- Data Link Layer

The second layer in the Open Systems Interconnection (OSI) model, providing transparent and reliable information transmission services between adjacent nodes.

- Application Layer

The seventh layer in the Open Systems Interconnection (OSI) model, implementing specific functions for data manipulation and information exchange.

- Frame

In data and digital communication, a specific information structure composed of a predetermined number of bits or fields according to a certain standard. Data is transmitted over the network in small units called frames. A frame consists of several parts, and different parts perform different functions.

#### Physical Layer

| Physical layer parameters | Physical layer content | Remarks |
| --- | --- | --- |
| Communication method | RS485 | Half-duplex |
| Communication Address | 1~247 selectable | Default: 3 |
| Communication Baud Rate | 4.8kbps\9.6kbps\19.2kbps\38.4kbps selectable | Default: 9.6kbps |
| Communication Distance | ≤ 1000 m | At low baud rates |
| Communication Medium | Shielded twisted pair | Class A |

2 / 12

#### Data Link Layer

Transmission mode: Master-slave half-duplex mode (master queries, slave responds). Protocol type: The communication protocol adopts the Modbus-RTU method.

    - Serial Transmission Format

One frame of data contains: 1 start bit, 8 data bits, 1 parity bit, 1 stop bit.

| Start | Data |  |  |  |  |  |  |  | Parity Bit | Stop |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 1 |

    - Data Packet (Multi-Frame) Format

| Start | Address Frame | Function Frame | Data Frame | Check Frame | End |
| --- | --- | --- | --- | --- | --- |
| T3.5 | 8 bits | 8 bits | n×8 bits | 16 bits | T3.5 |

In RTU mode, the start of a message requires at least a silent interval of 3.5 characters (or frames). Based on the baud rate used, this silent interval time (e.g., T3.5 in the above table) can be easily calculated. This delay needs to be considered when implementing the communication protocol using a microcontroller's UART. If using configuration software or a DCS where the underlying software already handles this, it may not need to be considered during use.

The time interval between multiple data packets is recommended to be more than 200 ms. A sending period below 100 ms may lead to an increased packet loss rate.

#### Application Layer

The application layer parses the data packet (including address code, function code, data field, check code, etc.) to achieve the purpose of data exchange. The format is as follows:

| Address Code | Function Code | Register Start Address |  | Number of Variables |  | CRC Check Code |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | High Byte | Low Byte | High Byte | Low Byte | Low Byte | High Byte |
| 03H | 03H | 00H | 06H | 00H | 03H | E4H | 28H |

#### Address Code

The address code is at the beginning of the data packet, consisting of 8 bits (value 1-247). The default address code is 3.

The address code specifies the address of the user-defined slave device, which will receive data from the master station connected to it.

In the same network, the address of each slave device must be unique. Only the addressed slave will respond to a query containing that address. When a slave sends back a response, the slave address data in the response informs the master which slave is communicating with it.

### When the master sends an incorrect communication address to a slave, the slave will not respond.

#### Function Code

The function code tells the addressed slave what function to perform. The function codes sent by the master are listed in the table below:

| Function code | Definition | Function behavior |
| --- | --- | --- |
| 03H | Read Data Register | Reads the data value of one or more registers |
| 06H | Write Single Register | Writes data to a register |

For details, see 3 Function Codes

.

#### Data Field

The data field contains the data required by the slave to perform a specific function or the data collected by the slave when responding to a query. The content of this data may be values, reference addresses, or limit values. For specific content, refer to the communication address register table.

For example: A function code tells the slave to read a register. The data field then needs to specify from which register to start and how many data points to read. The embedded addresses and data vary according to the type and the different capabilities of the slaves.

3 / 12

#### Check Code

This field allows the master and slave to check for errors during transmission. Sometimes, due to electrical noise and other interferences, a set of data may undergo some changes on the line when transmitted from one device to another. Error checking ensures that the master or slave does not respond to data that has been altered during transmission, thereby improving system security and efficiency. The error checking uses a 16-bit cyclic redundancy method.

The Cyclic Redundancy Check (CRC) field occupies two bytes and contains a 16-bit binary value. During transmission, the low byte is sent first, followed by the high byte.

The CRC value is calculated by the transmitting device and then appended to the data frame. The receiving device recalculates the CRC value upon receiving the data and then compares it with the value in the received CRC field. If these two values are not equal, an error has occurred.

The generation method for CRC16 is detailed in Appendix A: CRC-16 Generation Principle.

#### Function Code

| Function Code | Definition | Function Behavior |
| --- | --- | --- |
| 03H | Read Data Register | Reads the data value of one or more registers |
| 06H | Write Single Register | Writes data to a register |
| 83H | Read Register Exception | The master sends an abnormal command 03, and the slave responds with an error function code. |
| 86H | Write Register Exception | The master sends an abnormal command 06, and the slave responds with an error function code. |

When the master sends a command with function code 03H, under normal circumstances, the slave responds with function code 03H. In case of an error, the slave responds with 83H.

When the master sends a command with function code 06H, under normal circumstances, the slave responds with function code 06H. In case of an error, the slave responds with 86H.

When the master sends an erroneous information frame to the slave (such as incorrect communication address, wrong check code, or an incomplete frame), the slave does not respond.

#### Read Data Registers (03H)

### Function code 03H allows users to obtain data and system parameters collected and recorded by the controller.

| Master Query |  |  |  | Slave Response |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Frame Field | Content | Description |  | Frame Field | Content | Description |  |
| Address Code | 03 | Slave Address |  | Address Code | 03 | Slave Address |  |
| Function Code | 03 | Function Code |  | Function Code | 03 | Function Code |  |
| Data Field | 00 | Read Register Address | High Byte | Data Field | 06 | Total Bytes of Returned Data |  |
|  | 06 |  | Low Byte |  | 00 | Data 1 | High Byte |
|  | 00 | Number of Data to Read | High Byte |  | DC |  | Low Byte |
|  | 03 |  | Low Byte |  | 00 | Data 2 | High Byte |
| Check Code | E4 | CRC Check | Low Byte |  | E6 |  | Low Byte |
|  | 28 |  | High Byte |  | 00 | Data 3 | High Byte |
|  |  |  |  |  | F0 |  | Low Byte |
|  |  |  |  | Check Code | 08 | CRC Check | Low Byte |
|  |  |  |  |  | 75 |  | High Byte |

Example:

Read the three-phase voltage values (A, B, C) of Power Supply I. The returned results are Uan=220V, Ubn=230V, Ucn=240V. The master sends [ 03 03 00 06 00 03 E4 28 ]

The slave responds [ 03 03 06 00 DC 00 E6 00 F0 08 75 ]

4 / 12

#### Write Single Register (06H)

Function code 06H allows users to modify the content of a single register. Any writable register inside the controller can have its value changed using this function code.

| Master query |  |  |  | Slave response |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Frame field | Content | Description |  | Frame field | Content | Description |  |
| Address code | 03 | Slave Address |  | Address code | 03 | Slave Address |  |
| Function code | 06 | Function Code |  | Function code | 06 | Function Code |  |
| Data field | 20 | Register Address to Write | High Byte | Data field | 20 | Write Register Address | High Byte |
|  | 65 |  | Low Byte |  | 65 |  | Low Byte |
|  | 00 | Write Data | High Byte |  | 00 | Write Data | High Byte |
|  | A0 |  | Low Byte |  | A0 |  | Low Byte |
| Check code | 93 | CRC Check | Low Byte | Check code | 93 | CRC Check | Low Byte |
|  | 8F |  | High Byte |  | 8F |  | High Byte |

Example:

For the NXZ(H)MN series, modify the undervoltage setting value for Power Supply I (register address is 0x2065) to 160V (hexadecimal is 0x00A0).

The master sends [ 03 06 20 65 00 A0 93 8F ]

The slave responds [ 03 06 20 65 00 A0 93 8F ]

#### Error Handling

When the master sends an erroneous information frame to the slave (such as incorrect function code, wrong register address, incorrect data, or lack of modification permission), the slave returns corresponding error information. If the master sends an erroneous command with function code 03H, the slave responds with function code 83H. If the master sends an erroneous command with function code 06H, the slave responds with function code 86H.

Specific error reasons: 01: Illegal data; 02: Wrong register address; 03: Data length error.

| Master Query |  |  |  |  | Slave Response |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Frame Field | Content |  | Description |  | Frame Field | Content |  | Description |  |
| Address Code | 03 | Slave Address |  |  | Address code | 03 | Slave Address |  |  |
| Function code | 03 | Function Code |  |  | Function code | 83 | Function Code. Due to an error, the function code's highest bit is set to 1 |  |  |
| Data field | A8 | Read Register Address |  | High Byte | Data field | 02 | Error Reason: 01: Illegal Data; 02: Register Address Error; 03: Data Length Error. |  |  |
|  | 00 |  |  | Low Byte | Check code | 61 | CRC Check |  | Low Byte |
|  | 00 | Number of Data to Read |  | High Byte |  | 31 |  |  | High Byte |
|  | 01 |  |  | Low Byte |  |  |  |  |  |
| Check code | A5 | CRC Check |  | Low Byte |  |  |  |  |  |
|  | 88 |  |  | High Byte |  |  |  |  |  |

Example:

The master requests to read data from a non-existent address. After the controller determines the data error, it returns the corresponding function code 83H (the highest bit of the function code 03H sent by the master is set to 1 as the slave's response function code), with error reason 02H (wrong register address).

5 / 12

#### Communication Data Registers

#### Dataset

| No. | Parameter Item | Data Type | Unit | Access Rule | Register Address | Parameter Description | Applicable Products |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | NL1 Phase Voltage | UINT | V | R | 0x0006 | Power Supply I, Phase A Voltage | All |
| 2 | NL2 Phase Voltage | UINT | V | R | 0x0007 | Phase B voltage of Power Supply I | All |
| 3 | NL3 Phase Voltage | UINT | V | R | 0x0008 | Phase C voltage of Power Supply I | All |
| 4 | RL1 Phase Voltage | UINT | V | R | 0x0009 | Phase A voltage of Power Supply II | All |
| 5 | RL2 Phase Voltage | UINT | V | R | 0x000A | Phase B voltage of Power Supply II | All |
| 6 | RL3 Phase Voltage | UINT | V | R | 0x000B | Phase C voltage of Power Supply II | All |
| 7 | Software Version Number | UINT | \ | R | 0x000C | Software Version Number | All |
| 8 | Frequency | UINT | Hz | R | 0x000D | Power supply frequency, see section 4.2 Power Frequency Register for details. | NXZ(H)MN /NZ5(H)M |
| 9 | Modbus Parity Bit | UINT | \ | R\W | Ox000E | 0: No parity (None) 1: Odd parity (Odd) 2: Even parity (Even) Default: 2 Even parity (Even) | All |
| 10 | MAX-N-A Phase Voltage | UINT | V | R | 0x000F | Maximum Phase A voltage of Power Supply I | All |
| 11 | MAX-N-B Phase Voltage | UINT | V | R | 0x0010 | Maximum Phase B voltage of Power Supply I | All |
| 12 | MAX-N-C Phase Voltage | UINT | V | R | 0x0011 | Maximum Phase C voltage of Power Supply I | All |
| 13 | MAX-R-A Phase Voltage | UINT | V | R | 0x0012 | Maximum Phase A voltage of Power Supply II | All |
| 14 | MAX-R-B Phase Voltage | UINT | V | R | 0x0013 | Maximum Phase B voltage of Power Supply II | All |
| 15 | MAX-R-C Phase Voltage | UINT | V | R | 0x0014 | Maximum Phase C voltage of Power Supply II | All |
| 16 | Power Supply I Side Switching Count | UINT | \ | R | 0x0015 | Switch switching count of Power Supply I | All |
| 17 | Power Supply II Side Switching Count | UINT | \ | R | 0x0016 | Switch switching count of Power Supply II | All |
| 18 | Total Operating Time | UINT | h | R | 0x0017 | Operating Time (Cleared upon power-off) | All |
| 19 | Modbus Address | UINT | \ | R/W | 0x0100 | Address range: 1~247, Default: 3 | All |
| 20 | Modbus Baud Rate | UINT | kbps | R/W | 0x0101 | 0:4.8 kbps 1:9.6 kbps 2:19.2 kbps 3：38.4 kbps Default: 1:9.6 kbps | All |
| 21 | Power Supply I, Power Supply II Status | UINT | \ | R | 0x004F | Power supply status, for details see section 4.3 Power Status Register | All |
| 22 | Switch status | UINT | \ | R | 0x0050 | Switch status, for details see section 4.4 Switch Status Register | All |
| 23 | Power supply I undervoltage action threshold setting Value U1 | UINT | V | R/W | 0x2065 | Setting range: 150~200V | NXZ(H)MN /NZ5(H)M |

6 / 12

| No. | Parameter Item | Data Type | Unit | Access Rule | Register Address | Parameter Description | Applicable Products |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 24 | Power supply II undervoltage action threshold setting Value U2 | UINT | V | R/W | 0x2066 | Setting range: 150~200V | NXZ(H)MN /NZ5(H)M |
| 25 | Power supply I overvoltage Action threshold setting value U3 | UINT | V | R/W | 0x2067 | Setting range: 240~290V | NXZ(H)MN /NZ5(H)M |
| 26 | Power supply II overvoltage action threshold setting value U4 | UINT | V | R/W | 0x2068 | Setting range: 240~290V | NXZ(H)MN /NZ5(H)M |
| 27 | Transfer delay time setting value T1 | UINT | 1s | R | 0x2069 | 0~30s, read-only | NXZ(H)BN /NZ5(H)B |
|  |  | UINT | 1s | R/W |  | 0~180, default: 5s | NXZ(H)MN /NZ5(H)M |
| 28 | Return delay time setting value T2 | UINT | 1s | R | 0x206A | 0~30s, read-only | NXZ(H)BN /NZ5(H)B |
|  |  | UINT | 1s | R/W |  | 0~180, default: 5s | NXZ(H)MN /NZ5(H)M |
| 29 | Generator start delay T3 | UINT | 1s | R/W | 0x206B | 0~180, default: 5s | NXZ(H)MN /NZ5(H)M |
| 30 | Generator shutdown delay T4 | UINT | 1s | R/W | 0x206C | 0~180, default: 5s | NXZ(H)MN /NZ5(H)M |
| 31 | Mode selection | UINT | \ | R/W | 0x206D | 0: Auto-transfer with automatic restoration 1: Auto-transfer without automatic restoration 2: Mutual backup 3: Auto-transfer with automatic restoration (generator) 4: Auto-transfer without automatic restoration (generator) 5: Mutual backup (generator) Default 0: Auto-transfer with automatic restoration | NXZ(H)MN /NZ5(H)M |
|  |  |  |  | R |  | 1: Auto-transfer with automatic restoration 2: Auto-transfer without automatic restoration 3: Mutual backup 4: Test mode Default 1: Auto-transfer with automatic restoration | NXZ(H)BN /NZ5(H)B |
| 32 | Forced transfer command | UINT | \ | W | 0x2700 | Forced transfer function, for details see section 4.6 Forced Transfer Re gister | All |
| 33 | Control command | UINT | \ | W | 0x2800 | Control function, for details see section 4.5 Control Command Register |  |

Data type: "UINT" represents unsigned integer, occupying two bytes.

Access rules: "R" represents read-only, "R/W" represents readable and writable, "W" represents write-only. Register address: For programming convenience, represented in hexadecimal.

Applicable products: "All" means all series products are supported; "NXZ(H)MN" represents NXZMN, NXZHMN models; "NZ5(H)M" representsNZ5M, NZ5HM models; "NXZ(H)BN" represents NXZBN, NXZHBN models; "NZ5(H)B" represents NZ5B, NZ5HB models.

7 / 12

#### Power Frequency Registers

| Power supply frequency (address: 0x000D) read-only |  |
| --- | --- |
| Bit15 ~ Bit8 | Bit7~ Bit0 |
| Power supply I frequency, unit: Hz | Power supply II frequency, unit: Hz |

### Only NXZ(H)MN\NZ5(H)M series products support this command.

Example: Power Supply I frequency is 50Hz, Power Supply II frequency is 0Hz. The master sends [ 03 03 00 0D 00 01 14 2B ]

### The slave responds [ 03 03 02 32 00 D4 E4 ]

#### Power Status Registers

| Power supply status (address: 0x004F) read-only |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Bit15 | Bit14 | Bit13 | Bit12 | Bit11 | Bit10 | Bit9 | Bit8 |
| Reserved | Reserved | Phase C voltage of Power Supply I 00: Normal, 01: Undervoltage 10: Overvoltage |  | Phase B voltage of Power Supply I 00: Normal, 01: Undervoltage 10: Overvoltage |  | Power Supply I, Phase A Voltage 00: Normal, 01: Undervoltage 10: Overvoltage |  |
| Bit7 | Bit6 | Bit5 | Bit4 | Bit3 | Bit2 | Bit1 | Bit0 |
| Reserved | Reserved | Phase C voltage of Power Supply II 00: Normal, 01: Undervoltage 10: Overvoltage |  | Phase B voltage of Power Supply II 00: Normal, 01: Undervoltage 10: Overvoltage |  | Phase A voltage of Power Supply II 00: Normal, 01: Undervoltage 10: Overvoltage |  |

Example: All three-phase voltages of Power Supply I are normal, while all three-phase voltages of Power Supply II are undervoltage. The master sends [ 03 03 00 4F 00 01 B4 3F ]

### The slave responds [ 03 03 02 00 15 0F 17 ]

#### Switch Status Registers

| Switch status (Address: 0x0050) Read-only |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Bit15 | Bit14 | Bit13 | Bit12 | Bit11 | Bit10 | Bit9 | Bit8 |
| Reserved | Reserved | Reserved | Reserved | Reserved | Reserved | Reserved | Whether remote control 0: No 1: Yes |
| Bit7 | Bit6 | Bit5 | Bit4 | Bit3 | Bit2 | Bit1 | Bit0 |
| Fault type: 000: None |  |  |  |  | Intermediate position (Double-off position) 0: No 1: Yes |  |  |
| 001: Fire-fighting linkage |  |  |  |  |  | Generator status |  |
| 010: Motor timeout |  |  | Power Supply I side | Power Supply II side |  | Status |  |
| 011: Power Supply I tripped 100: Power Supply II tripped |  |  | Switch position 0: Open | Switch position 0: Open |  | 0 : Generator Unit shut down | 0: Manual mode 1: Automatic mode |
| 101: Abnormal closing signal |  |  | 1: Close | 1: Close |  | 1 : Generator |  |
| 110: Power Supply I phase sequence abnormal |  |  |  |  |  | Unit start-up |  |
| 111: Power Supply II phase sequence abnormal |  |  |  |  |  |  |  |

### Example: Power Supply I side is open, Power Supply II side is closed, the generator is off, and it is in automatic mode. The master sends [ 03 03 00 50 00 01 85 F9 ]

The slave responds [ 03 03 02 00 11 01 88 ]

8 / 12

#### Control Command Registers

| Control command (Address: 0x2800) Write-only |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Bit15 | Bit14 | Bit13 | Bit12 | Bit11 | Bit10 | Bit9 | Bit8 |
| Reserved | Reserved | Reserved | Reserved | Reserved | Reserved | Reserved | Reserved |
| Bit7 | Bit6 | Bit5 | Bit4 | Bit3 | Bit2 | Bit1 | Bit0 |
| Reserved | Reserved | Clear motor timeout fault 0: No 1: Yes | Clear fire-fighting fault 0: No 1: Yes | Reserved | Remote Control 0: None 1: remote control | Parameter Setting 0: None 1: Restore Default Parameters | History Record Setting 0: None 1: Clear History Record |

Example:

- Restore default parameters (including baud rate, communication address, and other configurations). The master sends [ 03 06 28 00 00 02 00 49 ]

The slave responds [ 03 06 28 00 00 02 00 49 ]

- Clear historical records (including switching count, maximum phase voltage). The master sends [ 03 06 28 00 00 01 40 48 ]

The slave responds [ 03 06 28 00 00 01 40 48 ]

#### Forced Transfer Registers

The forced transfer command can only be used in remote control state. That is, a control command (address:

0x2800) must be sent first to enter the remote control state.

| Forced Transfer Command (Address: 0x2700) Write Only |  |  |  |
| --- | --- | --- | --- |
| 0x0000 | Forced Transfer to Power Source I Position | Effective when in 'Remote Control State' | During forced transfer, i.e., when needing to switch to close a circuit with a specific power source, the voltage of that power source must be in a normal state for the product to execute the corresponding action. |
| 0x00aa | Forced Transfer to Power Source II Position |  |  |
| 0x00ff | Forced Transfer to Double Disconnect Position |  |  |

For NXZ(H)MN\NZ5(H)M series products, during remote control, the remote lock must be in the OFF state (default is OFF). That is, on the controller display panel, press the setting key, page through the keys, enter submenu "A-F", and set it to OFF. Example:

1. Enter remote control

Master sends [03 06 28 00 00 04 80 4B]

Slave responds [03 06 28 00 00 04 80 4B]

2. Forced transfer to double disconnect

Master sends [03 06 27 00 00 FF C2 DC]

Slave responds [03 06 27 00 00 FF C2 DC]

3. Forced transfer to power source I

Master sends [03 06 27 00 00 FF 82 9C]

Slave responds [03 06 27 00 00 FF 82 9C]

4. Forced transfer to power source II

Master sends [03 06 27 00 00 AA 02 EC]

Slave responds [03 06 27 00 00 AA 02 EC]

5. Exit remote control

Master sends [03 06 28 00 00 00 81 88]

Slave responds [03 06 28 00 00 00 81 88]

9 / 12

#### Communication connection method

#### Hardware connection

Reliably connect the A, B, and GND lines in the RS485 bus to the controller's (A+), (B-), and (GND) terminals respectively. Then, power up Power Supply I or Power Supply II normally, or use an external power supply to ensure the controller is powered normally.

#### Communication parameter configuration

Ensure the communication parameters of the host computer and the controller are consistent. There are 6 types of communication parameters in total: 3 adjustable parameters (communication address, baud rate, parity bit) and 3 fixed parameters (data bits, stop bits, flow control). For details, see the table below.

| No. | Communication Parameters | Default Value | Value Range | Register Address | Setting Menu (Only for NXZ(H)MN, NZ5(H)M) |
| --- | --- | --- | --- | --- | --- |
| 1 | Communication Address | 3 | 1～247 | 0x0100 | On the controller display panel, press the setting key, press the key to page down, enter the sub-menu "A-A", press "+" or "-" keys to modify parameters. Press the setting key again to exit. |
| 2 | Baud Rate | 1:9.6 kbps | 0:4.8 kbps 1:9.6 kbps 2:19.2 kbps 3：38.4 kbps | 0x0101 | On the controller display panel, press the setting key, press the key to page down, enter the sub-menu "A-C", press "+" or "-" keys to modify parameters. Press the setting key again to exit. |
| 3 | Parity Bit | 2: Even parity (Even) | 0: No parity (None) 1: Odd parity (Odd) 2: Even parity (Even) | 0x000E | On the controller display panel, press the setting key, press the key to page down, enter the sub-menu "A-E", press "+" or "-" keys to modify parameters. Press the setting key again to exit. |
| 4 | Data Bit | 8 | Fixed parameter, not adjustable | / | / |
| 5 | Stop Bit | 1 | Fixed parameter, not adjustable | / | / |
| 6 | Flow Control | None | Fixed parameter, not adjustable | / | / |

For NXZ(H)MN and NZ5(H)M series products, the adjustable communication parameters can be set on the product's display panel.

For NXZ(H)BN and NZ5(H)B series products, as there is no display panel, communication parameters cannot be set via menu. Therefore, it is generally not recommended to modify the communication parameters. If modification is necessary, communication connection must be established first, and then use Modbus write commands to modify the parameters; to restore the communication parameters to default, input the fire signal for more than 60 seconds.

#### Communication anomaly troubleshooting

    - Check hardware: whether the RS485 communication bus A, B and the controller's terminals (A+), (B-) are loose or reversed; check if the power supply is normal.

    - Check if the communication parameter settings of the automatic transfer switch controller are correct (must be consistent with the host computer). NXZ(H)MN, NZ5(H)M series products can set the adjustable communication parameters on the product's display panel. NXZ(H)BN, NZ5(H)B series products can input the fire signal for more than 60 seconds to restore communication parameters to default.

    - Check if the serial port parameter settings in the communication host (debugger) are correct (must be consistent with the controller parameters).

    - Check if the communication adapter (RS485 converter) is damaged (test with a new one).

    - If there are no issues with the above situations, you can contact our company for further analysis.

10 / 12

### Appendix A CRC-16 generation principle

During CRC calculation, first preset a 16-bit register to all 1s, then continuously perform operations on the 8-bit characters in the data frame and the current value of this register. Only the 8 data bits of each byte participate in generating the CRC; start bits, stop bits, and any parity bits used do not affect the CRC.

When generating the CRC, each 8-bit character is XORed with the contents of the register, then the result is shifted to the low-order bits, the high-order bits are filled with "0", the least significant bit (LSB) is shifted out and checked. If it is 1, the register undergoes an XOR operation with a preset fixed value; if the LSB is 0, no processing is done.

The above process is repeated until eight shift operations have been completed. After the last bit (the 8th bit) has been shifted out, the next 8-bit character is XORed with the current value of the register, and another eight shifts and XOR operations as described above are performed. When all bytes in the data frame have been processed, the final value generated is the CRC value.

The process to generate a CRC is as follows:

- Preset a 16-bit register to the value FFFFH (all 1s), called the CRC register;

- XOR the first 8-bit character in the data frame with the low byte of the CRC register, and store the result back in the

CRC register;

- Shift the CRC register one bit to the right, fill the highest bit with 0, shift out and check the least significant bit;

- If the LSB is 0: repeat step three (next shift);

- If the LSB is 1: XOR the CRC register with a preset fixed value (0A001H);

- Repeat steps three and four until 8 shifts are completed. This completes the processing of one full eight-bit character;

- Repeat steps 2 to 5 to process the next 8-bit character until all bytes are processed;

- The final content of the CRC register is the CRC value.

11 / 12

### Appendix B NXZ(H)MN communication application cases

--- Achieving remote control transfer to the double-open position

- Power and communication wiring: First, reliably connect the A, B, and GND lines in the RS485 bus to the automatic transfer switch controller's (A+),

(B-), (G) terminals respectively; then, power up Power Supply I or Power Supply II normally to ensure the controller is powered normally.

- Connect the RS485 bus converter to the debugging computer.

- Ensure the communication parameters of the host computer and the controller are consistent. This time, the controller's default communication parameters are used: baud rate 9.6kbps, even parity, communication address 3.

- Open the serial port debugging tool, set the serial port number according to the actual situation; configure the serial port parameters as: baud rate 9.6kbps, 1 start bit,

8 data bits, even parity, and 1 stop bit.

- Read function test: Send test frame (03 03 00 4F 00 01 B4 3F). If the controller returns data starting with 03 03 02, it indicates the read function is normal. For all register addresses, see 4.1 Data Set.

- Write function test: Send test frame (03 06 28 00 00 04 80 4B). If the controller returns (03 06 28 00 00 04 80 4B) data, and the controller screen's "Manual" and "Auto" indicators flash simultaneously, it indicates communication is normal and it has entered the "Remote Control State".

- Write function test: Send test frame (03 06 27 00 00 FF C2 DC). The controller returns (03 06 27 00 00 FF C2 DC), and simultaneously the product is forced to transfer to the double-open position (middle position). For details, see 4.6 Forced Transfer Register.

- If communication is abnormal, refer to 5.3 Communication Anomaly Troubleshooting for investigation items.